## Cubical
Feeders
№ | Type | Description | In distribution busbar (A) | Incomers | >630А | <=630А | MCC
1 | 230 | Very high power incomers / feeders cubicle | 4500 | NW40b | NW40b | NO | NO
|  |  | 7300 | NW63b | NW63b
2 | 115 | High power incomers / feeders cubicle | 1750 | NT08 | NT08 | NO | NO
|  |  | 4000 | NT10 | NT10
|  |  |  | NT12 | NT12
|  |  |  | NT16 | NT16
|  |  |  | NW08 | NW08
|  |  |  | NW10 | NW10
|  |  |  | NW12 | NW12
|  |  |  | NW16 | NW16
|  |  |  | NS800 | NS800
|  |  |  | NS1000 | NS1000
|  |  |  | NS1250 | NS1250
|  |  |  | NS1600 | NS1600
3 | 115/70-2 | Mixed incomers / feeders cubicle | 1750 | NT08 | NT08 | disconnectable mounting plate | NO
|  |  | 3200 | NT10 | NT10 | disconnectable Polyfast
|  |  |  | NT12 | NT12 | plug-in Polyfast
|  |  |  | NT16 | NT16 | drawer
|  |  |  | NW08 | NW08
|  |  |  | NW10 | NW10
|  |  |  | NW12 | NW12
|  |  |  | NW16 | NW16
|  |  |  | NS800 | NS800
|  |  |  | NS1000 | NS1000
|  |  |  | NS1250 | NS1250
|  |  |  | NS1600 | NS1600
4 | Single NW | Optimized high power incomers / feeders cubicle | 1600 | NW08 | NW08 | NO | NO
|  |  | 3200 | NW10 | NW10
|  |  |  | NW12 | NW12
|  |  |  | NW16 | NW16
|  |  |  | NW20 | NW20
|  |  |  | NW25 | NW25
|  |  |  | NW32 | NW32
5 | Single NT / NS | Optimized high power incomers / feeders cubicle | 800 | NT08 | NT08 | NO | NO
|  |  | 1600 | NT10 | NT10
|  |  |  | NT12 | NT12
|  |  |  | NT16 | NT16
|  |  |  | NS800 | NS800
|  |  |  | NS1000 | NS1000
|  |  |  | NS1250 | NS1250
|  |  |  | NS1600 | NS1600
6 | PFC | Compensation & harmonic filtering | NO | NO | NO | Power factor compensation | NO
7 | 185 | Fuse-switch feeders cubicle | NO | NO | NO | Jean Müller | NO
8 | 70-2 | Electrical distribution drawers | 1000 | NT08 | NT08 | disconnectable mounting plate | disconnectable mounting plate <= 37 kW
|  |  | 2100 | NT10 | NT10 | disconnectable Polyfast | drawer <= 250 kW
|  |  |  | NT12 | NT12 | plug-in Polyfast
|  |  |  | NT16 | NT16 | drawer
|  |  |  | NS800 | NS800
|  |  |  | NS1000 | NS1000
|  |  |  | NS1250 | NS1250
|  |  |  | NS1600 | NS1600
9 | 70-F | Electrical distribution feeders cubicle | 2100 | NT08 | NT08 | fixed mounting plate for 1 NSX or NS100-630 | NO
|  |  |  | NT10 | NT10 | fixed mounting plate for 2 NSX100-250
|  |  |  | NT12 | NT12
|  |  |  | NT16 | NT16
10 | VSD - SS | [5 empty] | fixed mounting plate <= 400 kW
drawer <= 55 kW

## Feeders Service Index
|  | Operation Setting Locking Padlocking | Maintenance Checking Cleaning Repairing | Evolution Addition Modifications Expansion
1 | Not required | Shutting down the whole switchboard | Shutting down the whole switchboard | Shutting down the whole switchboard
2 | Wanted | Shutting down only the concerned FU | Shutting down only the concerned FU with connections handling | Addition of a FU in pre-equiped spare slots
3 | Essential | Shutting down only the concerned FU Allows “test” position | Shutting down only the concerned FU without connections handling | Addition of a FU without shutting down the swwitchboard, free addition in non-equiped spare slots